## Pile Data Table
Pier / Bent | Pile Size & Type | Nominal Bearing Resistance (tons) | Tension Resistance (tons) | Minimum Tip Elevation (ft) | Test Pile Length / Pile Order Length (ft) | Required Jet Elevation (ft) | Required Preform Elevation (ft) | Factored Design Load (tons) | Downdrag (tons) | Total Scour Resistance (tons) | Net Scour Resistance (tons) | 100-Year Scour Elevation (ft) | Design Scour Elevation (temporary bridges) | Long-Term Scour Elevation (ft) | Resistance Factor | Pile Cut-Off Elevation (ft)
Pier | 20" Ø Pipe | 151 | N/A | N/A | N/A | N/A | N/A | 114 | N/A | N/A | N/A | N/A | N/A | N/A | 0.75 | 41.8

## Basis
Item | Basis
Support | Pier
Pile family | Steel pipe (noncomposite)
FBMP export | Pier_Fixed.XML
FBMP SHA-256 | 420e614aa8b9784b5f0e8160689f90d7480fec7dc3541ee7c687c5eadfd355e6
Source register | Matches PIER-XML
Factored Design Load, column I (tons) | 113.03 (maximum strength pile-head compression from FBMP, downdrag excluded)
Downdrag, column J (tons) | 0 per pile, drag load DR. Source: No downdrag at the pier (geotechnical engineer, 2026-10-19, user) (PENDING documentation)
Drag load factors | γDR = 1.1 at the strength limit states and 1 at Service I (LRFD Table 3.4.1-1); the geotechnical limit state uses DR = 0. The factored drag load enters the structural demands only; it is not part of column I.
Net scour resistance, column L (tons) | 0
Total scour resistance, column K (tons) | 0
Resistance factor φ, column P | 0.75 (SDG Table 3.5.7-1; footnote 7: Pile Data Tables use the default 0.75)
Nominal Bearing Resistance equation, column C | Rn = (Factored Design Load + Net Scour Resistance + Downdrag) / φ (SDG Eq. 3-1, Section 3.5.13)
Nominal Bearing Resistance (tons) | 150.71 computed; 151 in the table (rounded up)
Table 3.5.13-1 | Covers prestressed concrete piles only; confirm the driving resistance limit for the steel pipe with the geotechnical engineer.
Tension Resistance, column D (tons) | Maximum strength uplift from FBMP (7.45 tons)
Minimum Tip Elevation, column E | N/A until the handoff is received
Pile cut-off elevation, column Q | 41.7717 ft from the FBMP pile head, rounded to 0.1 ft
Rounding (SDG 3.5.15.D) | Loads up to the nearest ton; minimum tip elevations down and pile lengths up to the nearest foot; cut-off elevations to 0.1 ft.
Jet and preform elevations, columns G and H | Not applicable: no jetting or preforming is specified.
Design scour elevation, column N | Temporary bridges only: N/A.
Confirmation: exposure | PENDING · Environment classification confirmed for the SDG 1.4 covers, the Table 3.5.1-1 minimum size and the LRFD 5.9.2.3.2b tension limit used.
Confirmation: head_connection | PENDING · Pile-to-cap moment and uplift transfer with 12 in embedment verified in the coordinated detail (SDG 3.5.1.C, SDM 11.6).
Confirmation: steel_grade | Confirmed · Steel pipe grade and Fy reconciled: Spec 962 Table 962-11 A252 Gr 3 (45 ksi) against the Fy of the FBMP pile material.
Confirmation: corrosion | PENDING · Corrosion allowance and wall loss confirmed for the environment (LRFD 10.7.5, 5.12.9.5.2).
Confirmation: downdrag_source | PENDING · Downdrag of 18 tons per end-bent pile documented by the geotechnical engineer of record (neutral plane, scourable layers).
Confirmation: analysis_current | PENDING · FBMP export matches the selected cap case and the final rerun (COH-013, COH-028).
Confirmation: min_tip | PENDING · Minimum tip elevation received from the geotechnical handoff (SDG 3.5.9).
Confirmation: scour | PENDING · Scour resistance and scour elevations received from the hydraulics and geotechnical engineers.
Confirmation: drivability | PENDING · Drivability and driving stresses evaluated (LRFD 10.7.8, FDOT Specification 455); not computed here.

## Inputs
Input | Value | Unit | Meaning | Source | Status
D_pile | 20 | in | Pile size (square side, or pipe outside diameter) | PIER-XML Pier_Fixed.XML: section WIDTH | project source
N_pile | 4 |  | Piles in the support | PIER-XML Pier_Fixed.XML: PILE_GROUP piles | project source
S_pile | 5 | ft | Center-to-center pile spacing | PIER-XML Pier_Fixed.XML: pile head coordinates | project source
EL_cutoff | 41.7717 | ft | Pile cutoff elevation (FBMP pile head) | PIER-XML Pier_Fixed.XML: minus pile-head Z / 12 | project source
EL_ground | 26.05 | ft | Ground elevation (top of soil layer 1) | PIER-XML Pier_Fixed.XML: top of soil layer 1 | project source
L_unsupported | 15.7217 | ft | Length above ground (cutoff - ground); editable | PIER-XML Pier_Fixed.XML: cutoff - ground | project source
embed_cap | 12 | in | Pile embedment into the cap | Cap cases inputs.Pile_embed (12 in); SDG 3.5.1.C needs 48 in for full bending | project source
DD_tons | 0 |  | Downdrag (drag load DR) per pile, short tons | No downdrag at the pier (geotechnical engineer, 2026-10-19, user) | pending confirmation
gamma_DR_str | 1.1 |  | Drag-load factor, strength limit states (structural) | LRFD Table 3.4.1-1 | code
gamma_DR_ser | 1 |  | Drag-load factor, Service I | LRFD Table 3.4.1-1 | code
phi_geo | 0.75 |  | Geotechnical resistance factor (compression, Davisson) | SDG Table 3.5.7-1; footnote 7: Pile Data Tables use 0.75 | code
R_scour_net_tons | 0 |  | Net scour resistance, short tons | Scour not evaluated: geotechnical handoff | pending confirmation
R_scour_total_tons | 0 |  | Total scour resistance, short tons | Scour not evaluated: geotechnical handoff | pending confirmation
EL_scour_100 | N/A | ft | 100-year scour elevation (blank = N/A) | Geotechnical handoff | pending confirmation
EL_scour_LT | N/A | ft | Long-term scour elevation (blank = N/A) | Geotechnical handoff | pending confirmation
EL_min_tip | N/A | ft | Minimum tip elevation (blank = N/A) | Cap notebook geotech handoff (SDG 3.5.9) | pending confirmation
L_test_pile | N/A | ft | Test pile length (blank = N/A) | Not established | pending confirmation
K_eff | 1 |  | Effective length factor K | LRFD 10.7.3.13.4 pinned/fixed ends not established; FBMP P-delta preferred | code
soil_type | 0 |  | Soil for depth to fixity (0 sand, 1 clay) | LRFD C10.7.3.13.4 | pending confirmation
n_h | 0.556 | ksi/ft | Rate of increase of soil modulus, sand | LRFD Table C10.4.6.3-2, medium sand, submerged | code
S_u | 1 | kip/ft^2 | Undrained shear strength, clay (used only for soil type 1) | Placeholder: geotechnical report | pending confirmation
environment | 2 |  | Environment classification | SDG 1.4; same pending basis as the backwall notebook | pending confirmation
min_size_policy | 14 | in | Minimum square pile size, pedestrian bridge | SDG Table 3.5.1-1 (18 in with carbon-steel strand in Extremely Aggressive) | code
lambda_c | 1 |  | Concrete density modification factor | LRFD 5.4.2.8 normal weight | code
fc | 6.5 | ksi | Pile concrete strength f'c | FBMP XML FPC 6.5 ksi = FDOT Class V (Spec 346, 6,500 psi); 6.0 may be entered | project source
w_c | 0.15 | kip/ft^3 | Concrete unit weight (for Ec) | LRFD Table 3.5.1-1 normal weight | code
K_1 | 1 |  | Aggregate correction factor for Ec | LRFD 5.4.2.4 | code
f_pu | 270 | ksi | Strand ultimate strength (Grade 270 LRS) | Standard Plans Index 455-001 | code
f_py | 243 | ksi | Strand yield strength 0.9 fpu | LRFD Table 5.4.4.1-1 low-relaxation | code
E_p | 28500 | ksi | Strand modulus | LRFD 5.4.4.2 | code
loss_frac | 0.2 |  | Prestress loss as a fraction of the jacking force | Calibrated to the FBMP prestress 336 kip = 12 x 35 kip x 0.80 | project source
d_edge | 3.5 | in | Strand center distance from the pile face | Index 455-001 3 in cover; FBMP strand coordinates +-5.5 in on 18 in | project source
spiral_wire_area | 0.034 | in^2 | Spiral wire area (one leg) | Standard Plans Index 455-018 W3.4: W3.4 at 6 in full length; ends 16 turns at 3 in + 5 turns at 1 in | code
spiral_pitch | 6 | in | Spiral pitch | Index 455 spiral 6 in (ends 3 in and 1 in turns not used) | code
f_y_spiral | 70 | ksi | Spiral wire yield strength | ASTM A1064 wire; LRFD 5.7.2.5 permits up to 100 ksi; 60 ksi if preferred | pending confirmation
a_g | 0.75 | in | Maximum aggregate size | Class V concrete #67 stone, LRFD 5.7.3.4.2 | code
phi_v | 0.9 |  | Shear resistance factor, concrete | LRFD 5.5.4.2 | code
phi_c | 0.75 |  | Compression-controlled resistance factor | LRFD 5.5.4.2 | code
phi_t | 1 |  | Tension-controlled resistance factor, bonded prestressing | LRFD 5.5.4.2 | code
n_sweep | 121 |  | Neutral-axis sweep points for the interaction curve | Numerical setting (INFO) | code
D_out | 20 | in | Pipe outside diameter | PIER-XML Pier_Fixed.XML: section WIDTH | project source
t_wall | 0.48 | in | Pipe wall thickness (nominal) | PIER-XML Pier_Fixed.XML: SHELL_THICK | project source
t_corr | 0 | in | Corrosion allowance deducted from the wall | LRFD 10.7.5 / 5.12.9.5.2 (0.06 in): FDOT environment classification pending | pending confirmation
Fy | 45 | ksi | Steel yield strength | Spec 962 Table 962-11, ASTM A252 Gr 3; PIER-XML Pier_Fixed.XML pile material FY_SHELL 45 ksi equals this value | project source
E_s | 29000 | ksi | Steel modulus | LRFD 6.4.1 | code
phi_c_axial | 0.7 |  | Axial compression resistance factor, pipe (good driving, no tip) | LRFD 6.5.4.2 | code
phi_c_comb | 0.8 |  | Axial resistance factor, combined axial and flexure | LRFD 6.5.4.2 undamaged piles | code
phi_f | 1 |  | Flexure resistance factor | LRFD 6.5.4.2 | code
phi_v_steel | 1 |  | Shear resistance factor, steel | LRFD 6.5.4.2 | code
phi_y | 0.95 |  | Tension yielding resistance factor | LRFD 6.5.4.2, Eq. 6.8.2.1-1 | code
L_v | 15.7217 | ft | Shear span Lv (distance from maximum to zero shear) | PIER-XML Pier_Fixed.XML: cutoff - ground (default shear span) | project source